Siting and Land Rights

Right of Way & Permits

1123 West 3rd Avenue

Denver, Colorado 80223

Telephone: 303.571.3306

Facsimile: 303. 571. 3284

donna.l.george@xcelenergy.com

December 22, 2021

City of Littleton Community Development

2255 West Berry Avenue

Littleton, CO 80120

Attn:  	Elizabeth Kay Marchetti

Re:  	Goddard School, Case # SIP21-0001

Public Service Company of Colorado’s (PSCo) Right of Way & Permits Referral Desk has reviewed the site plan for Goddard School. Space consideration must be given to locate one or more pad mount transformers on this property with ground to sky clearance. The minimum space requirement per transformer is 12.5-feet by 12.5-feet, including a minimum clearance of 30-inches from non-combustible structures. Additional considerations are necessary if window, doors, or air vents are in close proximity to the proposed transformer location. Depending on the electric system that will serve this project, there may also be a requirement to provide a location with ground to sky clearance for an electric switch cabinet (minimum dimensions:  20’x 20’ or 15’ x 25’ depending on model) including a minimum of 5-10 feet from any obstructions. For details, please consult Xcel Energy’s Electric Standards located at:

https://www.xcelenergy.com/staticfiles/xe-responsive/Admin/Managed%20Documents%20&%20PDFs/Xcel-Energy-Standard-For-Electric-Installation-and-Use.pdf

Please be aware PSCo owns and operates existing electric distribution facilities within the subject property. The property owner/developer/contractor must complete the application process for any new natural gas or electric service including transformer, or modification to existing facilities via xcelenergy.com/InstallAndConnect. It is then the responsibility of the developer to contact the Designer assigned to the project for approval of design details.

Additional easements will need to be acquired by separate document for new facilities (i.e. transformer) – be sure to have the Designer contact a Right-of-Way and Permits Agent.

As a safety precaution, PSCo would like to remind the developer to call the Utility Notification Center by dialing 811 for utility locates prior to construction.

Donna George

Right of Way and Permits

Public Service Company of Colorado dba Xcel Energy

Office:  303-571-3306 – Email:  donna.l.george@xcelenergy.com